## Slide 1: EPICS V4 Expands Support to Physics Application, Data Acsuisition, and Data Analysis
L. Dalesio, Gabriele Carcassi, Martin Richard Kraimer, Nikolay Malitsky, Guobao Shen, Michael Davidsaver, BNL, Upton, Long Island, New York, U.S.A, Ralph Lange,Bessy, Berlin, Germany, Matej Sekoranja, Cosylab, Ljubljana, Slovenia, James Rowland, Diamond Light Source, Oxfordshire, England, Greg White, SLAC, Menlo Park, California, U.S.A. Timo Korhonen, PSI, Villigen, Switzerland.
ICALREPCS
October 14, 2011

## Slide 2: Outline
Version 3 recap
Version 4
Version 4 Architecture for Machine Control
Version 4 Architecture for Beam Line Control and DAQ
Conclusions

## Slide 3: Version 3 Supports Instrumentation
Records represented either an input signal, an output signal or an operation to perform on a set of signals
  Analog input, analog output, (multi-bit)binary input, (multi-bit) binary output, motor, event, PID, calc, etc…..
  Agreeing on what a device is – is difficult. Is it a power supply or a magnet? Does a motor have an LVDT, an encoder, back lash?
Records implement continuous control in an autonomous controller to perform DCS functionality.
Many different types of research and industrial facilities successfully applied this to their plant for equipment control.
Process Variables (PVs) are available across the network
  Any field of any record can be a process variable.
  Functions on PVs are: get, put, monitor
  This service was designed and implemented to be robust and fast (15K PVs per second to a client on a 100 MB network)
  Channels always have a time stamp, alarm severity, and alarm status – the simple data type was not useful in most cases
  Channels have metadata to describe display, control, and alarm information.
MANY clients were developed on this interface in many languages on many operating systems implementing the full range of SCADA capabilities.
  With two site developing EPICS, there were two display managers.

## Slide 4: Version 3 Has Limited Support for Devices
Records did not operate on things more complex than scalar signals.
  No time domain, no frequency domain, no images.
  No way to represent things more complicated than scalar signals and 1 dimensional arrays
Process Variables available across the network could not support everything needed
  No atomic command / response mechanism
  No way to ask for a PV subject to parameters.
  PVs metadata did not always fit properly for every field of a record – such as the display precision – what is the time stamp of this?
  Typically a get is done on connection for display, alarm limits, and control metadata changes are not reflected.
  Meta data was sent all of the time, so only time stamp and current alarm information is monitored.
MANY clients added layers on top of V3 Process Variables to implement more complex data models

## Slide 5: EPICS Version 3 Architecture
Distributed Front-Ends
MMLT, SDDS, XAL, SAD, CDEV, SPEC, GDA, etc…
Physical Device
Ethernet
EDM/MEDM/ DM2K/EDM/QT/IDL/ CSS
CAC
CAC
Other GUI tools
CAC
Diag Database
CAS
Physical Device
PS Database
CAS
Physical Device
RF Database
CAS
Physical Device
Vac Database
CAS
Physical Device
Util Database
CAS
C, C++, java, Matlab, SDDS, Python
CAC
Channel Archiver
CAC

## Slide 6: Version 4 Supports Complex Data Structures
Java IOC can represent devices
  We will likely not implement devices, as it is still difficult to agree on what these are
  We will use V3 records at NSLS II.
PVData (PVs) are available across the network
  Functions on PVs are: get, put, monitor, put/process/get (command/response)
  It is also hard to create object models on more complex devices such as a telescope or an accelerator.
Normative types are defined to provide metadata for more complex constructs: multi-channel array, table, N dimensional Array, Image.
  PVData always has a time stamp, alarm severity, and alarm status
  Vectors have useful metadata and distinctions: time domain vector, frequency domain vector, histogram
  Operations can be performed on two PVs with the same normative types.
  We have NOT
PVService supports creating middle layers services
MANY servers are being developed on this interface to implement middle layer through a collaboration for physics applications. A second collaboration is being established for beam line control, data acquisition, and data analysis.

## Slide 7
Specific Normative Data Types
NTMultichannelArray – represent a collection of single values as an ordered array
e.g. all of the temperatures along a beam line or the Australian Synch’s Concatenate Record used on AI’s
NTTimeDomainArray
e.g. a scope trace from a digitizer or the Circular Buffer in the Compress Record
NTHistogram e.g. information on a 60 Hz power supply RB posted every hour or the Histogram in the Compress Record
NTNDArray e.g. multiple frames of a detector taken at 1 KHz for 1 second
NTFrequencyDomainArray
e.g. FFT of 10 KHz data taken for 1 second to study noise frequencies or FFT record output
NTStatistic e.g. any data being compressed from its original rate – fast sampling in hardware to EPICS DB,
new function on any database waveform, response from a request to an archive server
NTImage e.g. image data being collected at a detector into the areaDetactor application
NTTable e.g. a way to return any list of values or collection of name, value pairs of different data type such as twiss parameters
or the metadata for a camera set up: filter, exposure time, camera used, etc…
This is the catch all data type that can define a structure of single values or arrays (of the same length)
NTChannelFinderDirectory
e.g. returned as an ordered list of PVs from a query to a directory service to populate a multi-channel array or table

## Slide 8: Applying Version 4 to Machine Control
Distributed Front-Ends
?Refactor? XAL, MMLT, SDDS, GDA
Physical Device
Ethernet
Thin HLA Client
CAC
CAC
Control System Studio
CAC
Diag Database
CAS
Physical Device
PS Database
CAS
Physical Device
RF Database
CAS
Physical Device
Vac Database
CAS
Physical Device
Util Database
CAS
Matlab, SDDS, Python
CAC
Diamond Simulation
Diag & PS
CAS
Channel Archiver View
PVManager
PVAS
Channel Finder Server
SQL
RDB
PVAC
PVAC
PVAS
PVAS
PVAS
PVAS
PVAS
PVAS
PVAS
Unit Conversion
CAC
PVAC
PVAS
Orbit
CAC
PVAS
Alignment, Magnet Map..
SQL
IRMIS
PVAC
Multichannel Array
PVAS
PVAC
PVAS
Archive Retrieval
XML/RPC
Channel
Archiver
PVAC

## Slide 9: Version 4 to Beam Line Control and DAQ
1) Request Parallel lanes for user FPGA
Spec, GDA, Edna etc…
Detector
Ethernet
Thin HLA Client
CAC
CAC
Control System Studio
CAC
Data Acq.
CAS
Channel Archiver View
PVManager
PVAS
Channel Finder Server
SQL
RDB
PVAC
PVAS
PVAS
Virtual Axis Conversion
CAC
PVAC
PVAS
Analysis
CAC
PVAS
Experiment Information.
SQL
IRMIS
PVAC
Multichannel Array
PVAS
PVAC
PVAS
Archive Retrieval
XML/RPC
Channel
Archiver
PVAC
N-lanes
Detector
Storage
User FPGA
Data Analysis.
CAS
PVAS
2) User FPGA Converts to NTType
3) Analysis In IOC creates resutls as NTType
4) Analysis In middle layer sevice creates resutls as NTType
5) Connect V4 client to existing codes

## Slide 10: Conclusions
  The interface is intended to allow us to create a standard client/server architecture for high level applications such as: areaDetector, Matlab Middle Layer Toolkit, SAD, SDDS, XAL, GDA, MDS+
  NSLSII is committed to apply this technology to physics applications, and is starting to apply it for applications in experiment control, data acquisition, and data analysis.
  Low level applications will be developed for large data sets in either the V4 Java IOC or by extending the V3 IOC to connect to PVAccess.
  New structures are easy to create – but we plan to carefully limit these to general and useful normative types.
  We are in the stage of development most similar to the early days of the EPICS collaboration: our first applications are being deployed, the normative types are not settled, there are still many challenges and lot of excitement.