## Slide 1: EPICS V4 Support to Physics Application, Data Acquisition, and Data Analysis
L. Dalesio, Gabriele Carcassi, Martin Richard Kraimer, Nikolay Malitsky, Guobao Shen, Michael Davidsaver, BNL, Upton, Long Island, New York, U.S.A, Ralph Lange,Bessy, Berlin, Germany, Matej Sekoranja, Cosylab, Ljubljana, Slovenia, James Rowland, Diamond Light Source, Oxfordshire, England, Greg White, SLAC, Menlo Park, California, U.S.A. Timo Korhonen, PSI, Villigen, Switzerland.
ICALREPCS
October 14, 2011

## Slide 2: Outline
Version 3 recap
Version 4
Version 4 Architecture for Machine Control
Version 4 Architecture for Beam Line Control and DAQ
Conclusions

## Slide 3: Version 3 Supports Instrumentation
Records represented either an input signal, an output signal or an operation to perform on a set of signals
  Analog input, analog output, (multi-bit)binary input, (multi-bit) binary output, motor, event, PID, calc, etc…..
  Agreeing on what a device is – is difficult. Is it a power supply or a magnet? Does a motor have an LVDT, an encoder, back lash?
Records implement continuous control in an autonomous controller to perform DCS functionality.
Many different types of research and industrial facilities successfully applied this to their plant for equipment control.
Process Variables (PVs) are available across the network
  Any field of any record can be a process variable.
  Functions on PVs are: get, put, monitor
  This service was designed and implemented to be robust and fast (15K PVs per second to a client on a 100 MB network)
  Channels always have a time stamp, alarm severity, and alarm status – the simple data type was not useful in most cases
  Channels have metadata to describe display, control, and alarm information.
MANY clients were developed on this interface in many languages on many operating systems implementing the full range of SCADA capabilities.
  With two site developing EPICS, there were two display managers.

## Slide 4: Version 3 Has Limited Support for Devices
Records did not operate on things more complex than scalar signals.
  No time domain, no frequency domain, no images.
  No way to represent things more complicated than scalar signals and 1 dimensional arrays
Process Variables available across the network could not support everything needed
  No atomic command / response mechanism
  No way to ask for a PV subject to parameters.
  PVs metadata did not always fit properly for every field of a record – such as the display precision – what is the time stamp of this?
  Typically a get is done on connection for display, alarm limits, and control metadata changes are not reflected.
  Meta data was sent all of the time, so only time stamp and current alarm information is monitored.
MANY clients added layers on top of V3 Process Variables to implement more complex data models

## Slide 5: EPICS Version 3 Architecture
Distributed Front-Ends
MMLT, SDDS, XAL, SAD, CDEV, SPEC, GDA, etc…
Physical Device
Ethernet
EDM/MEDM/ DM2K/EDM/QT/IDL/ CSS
CAC
CAC
Other GUI tools
CAC
Diag Database
CAS
Physical Device
PS Database
CAS
Physical Device
RF Database
CAS
Physical Device
Vac Database
CAS
Physical Device
Util Database
CAS
C, C++, java, Matlab, SDDS, Python
CAC
Channel Archiver
CAC

## Slide 6: Version 4 Supports Complex Data Structures
Java IOC can represent devices
  We will likely not implement devices, as it is still difficult to agree on what these are
  We will use V3 records at NSLS II.
PVData (PVs) are available across the network
  Functions on PVs are: get, put, monitor, put/process/get (command/response)
  It is also hard to create object models on more complex devices such as a telescope or an accelerator.
Normative types are defined to provide metadata for more complex constructs: multi-channel array, table, N dimensional Array, Image.
  PVData always has a time stamp, alarm severity, and alarm status
  Vectors have useful metadata and distinctions: time domain vector, frequency domain vector, histogram
  Operations can be performed on two PVs with the same normative types.
  We have NOT completed the work to resolve large data buffers
PVService supports creating middle layers services
MANY servers are being developed on this interface to implement middle layer through a collaboration for physics applications, beam line control, data acquisition, and data analysis.

## Slide 7: Applying Version 4 to Machine Control
Distributed Front-Ends
?Refactor? XAL, MMLT, SDDS, GDA
Physical Device
Ethernet
Thin HLA Client
CAC
CAC
Control System Studio
CAC
Diag Database
CAS
Physical Device
PS Database
CAS
Physical Device
RF Database
CAS
Physical Device
Vac Database
CAS
Physical Device
Util Database
CAS
Matlab, SDDS, Python
CAC
Diamond Simulation
Diag & PS
CAS
Channel Archiver View
PVManager
PVAS
Channel Finder Server
SQL
RDB
PVAC
PVAC
PVAS
PVAS
PVAS
PVAS
PVAS
PVAS
PVAS
Unit Conversion
CAC
PVAC
PVAS
Orbit
CAC
PVAS
SQL
RDB
PVAC
Model Server
PVAS
PVAC
PVAS
Archive Retrieval
XML/RPC
Channel
Archiver
PVAC
Lattic, Alignment, Magnet Map

## Slide 8: Version 4 to Beam Line Control and DAQ
1) Request Parallel lanes for user FPGA
Spec, GDA, Edna etc…
Detector
Ethernet
Thin HLA Client
CAC
CAC
Control System Studio
CAC
Data Acq.
CAS
Channel Archiver View
PVManager
PVAS
Channel Finder Server
SQL
RDB
PVAC
PVAS
PVAS
Virtual Axis Conversion
CAC
PVAC
PVAS
Analysis
CAC
PVAS
Experiment Information.
SQL
IRMIS
PVAC
Scan Service
PVAS
PVAC
PVAS
Archive Retrieval
XML/RPC
Channel
Archiver
PVAC
N-lanes
Detector
Storage
User FPGA
Data Analysis.
CAS
PVAS
2) User FPGA Converts to NTType
3) Analysis In IOC creates resutls as NTType
4) Analysis In middle layer sevice creates resutls as NTType
5) Connect V4 client to existing codes

## Slide 9: Science Support – Data Stores
Experiment
Planning
The Experiment Planning database provides information about the sample,
Equipment needed, scientist, etc… needed prior to the experiment
Experiment
Log Book
The Experiment Log Book contains information regarding the sample and
resultant scientific data. It includes logs for data taking, logs for analysis, and
Export file formats used to produce HDF5 files. Log entries can be made by the
Scientist or automatically by the experiment control or data analysis.
Scientific Data
The Scientific Data is the repository for large data sets. These data sets include
Matrices and image sets with the metadata required to plot or view the data. These
Are stored by sample and time stamp. Data can be written from experiment control
or submitted from analysis. Other data sets can also be sent here such as
Reference or model data.
Machine Data
Machine data is all time series data that is taken from the accelerator that is
available for use in analysis.
Beamline Data
Beamline data is all time series data that is taken from the end station, beam line,
Or accelerator that is available for use in analysis.

## Slide 10: Science Support – Proposed Development
Experiment
Planning
Experiment
Log Book
Scientific Data
Machine Data
Experiment & Safety Database
Measurements
Beamline Archiver
Beamline
Data
Machine Archiver
File Exporter
Analysis Processing
Data Management

## Slide 11
Driver
I/O Requirements::
Orbit from Cell Controllers – 180 BPMs (x, y, x’, y’, I + status + time?) @ 10 kHz
Turn by Turn Data – 180 BPMs for 230k turn @ on demand
Ripple detector Corrector power supplies - - 270 PS (10k 16 bit values) @ 1 Hz
Detectors – 8 GB / sec
Image Detector – 800 MB per second
Queue – 1 to n deep
Processing Block
PVAccess
Server
Queue – 1 to n deep
Driver scans or monitors into memory blocks
Large Data Sets - Requirements & Ability
Prototype the speed through an IOC
Prototype the speed for input into an IOC
PVAccess
Client
Prototype the speed over PVAccess

## Slide 12
Driver
Allocate memory for and read::
scalar (time stamped)
matrix (time stamped)
table (time stamped)
How to get aggregates into here – such as communication errors for an entire link or card?
time series of scalar, matrix, time series
Queue – 1 to n deep
Processing Block
Processing Block
Queue – 1 to n deep
Processing Block
Queue – 1 to n deep
PVAccess
Server
Queue – 1 to n deep
Configured from processing blocks – must understand hierarchy -
Driver scans or monitors into memory blocks
IOCs that Support Large Data Sets
PVAccess
Client
Develop optimized processing blocks (multi-core?)
Develop queuing mechanisms
Develop memory allocation schemes

## Slide 13: Conclusions
  The interface is intended to allow us to create a standard client/server architecture for high level applications such as: areaDetector, Matlab Middle Layer Toolkit, SAD, SDDS, XAL, GDA, MDS+
  NSLSII is committed to apply this technology to physics applications, experiment control, data acquisition, and data analysis.
  Low level applications will be developed for large data sets in either the V4 Java IOC or by extending the V3 IOC to connect to PVAccess.
  New structures are easy to create – but we plan to carefully limit these to general and useful normative types.
  We are in the stage of development most similar to the early days of the EPICS collaboration: our first applications are being deployed, the normative types are not settled, there are still many challenges.